## Sheet1
Vortex Enclosure Cooler - Sizing & Selection Worksheet
Height (in.)
| Width (in.) |  |  | Square Feet of Enclosure |  |  | 0
Depth (in.)
| Internal Temp. Now |  | Ambient Temp. Now |  |  | Delta T *F | 0
Vortex Cooler & Vortex A/C - BTUH Capacity
| Desired Internal Temp. |  | Worst Case Ambient |  |  | Delta T *F | 0 |  |  | AVAILABLE COMPRESSED AIR PRESSURE
|  |  | If internal and ambient temperatures are unknown, use dissipated heat in watts. |  |  |  |  | Enclosure Cooler Model Number |  | 60 PSIG** |  | 80 PSIG |  | 100 PSIG
| Dissipated Heat in Watts |  | Additional BTU's | 0 |  | Total Delta T *F | 0 |  |  | BTUH | >70 Deg. F | BTUH | >70 Deg. F | BTUH | >70 Deg. F
[8 empty] | 750 / 760 | NEMA 12 | 250 | 200 | 375 | 275 | 400 | 375
|  | Temp. Rise Due To Solar Radiation | [5 empty] | 730 / 740 | NEMA 12 | 600 | 375 | 775 | 525 | 900 | 700
|  | if enclosure is exposed to direct sunlight |  |  |  |  | Color Number | 780 / 790 | NEMA 12 | 750 | 625 | 1050 | 800 | 1500 | 1100
Number | Cabinet Color |  | Approx. Temp Rise |  |  |  |  | 785 / 795 | NEMA 12 | 1200 | 900 | 1600 | 1250 | 2500 | 1600
1 | White |  | 4 |  |  |  |  | 7870 / 7970 | NEMA 12 | 2400 | 1800 | 3200 | 2500 | 5000 | 3200
2 | Cream |  | 7 |  |  | Total BTUH | 0
3 | Yellow |  | 9 |  |  |  |  | 737 / 747 / 770-15H | NEMA 4 | 600 | 375 | 775 | 525 | 900 | 700
4 | Light Gray |  | 14 |  |  |  |  | 770 | NEMA 4 |  |  | 1050 | 800 | 1500 | 1100
5 | Medium Gray |  | 22 |  |  |  |  | 787 / 797 | NEMA 4 | 850 | 700 | 1120 | 900 | 1700 | 1300
6 | Dark Gray |  | 25 |  |  | CAPACITIES |  | 770-35H | NEMA 4 |  |  | 1600 | 1250 | 2500 | 1600
7 | Black |  | 27 |  |  |  |  | 787-35H / 797-35H | NEMA 4 | 1200 | 900 | 1600 | 1250 | 2500 | 1600
8 | National Aluminum or |  | 14 |  |  |  |  | 7875 / 7975 | NEMA 4 | 2400 | 1800 | 3200 | 2500 | 5000 | 3200
Stainless Steel
[6 empty] | Additional | BTU's | 737SS / 747SS / 7715 | NEMA 4X | 600 | 375 | 775 | 525 | 900 | 700
The cabinet is: |  | Sealed and unvented. |  |  |  | provided by | fan(s). | 7725 | NEMA 4X |  |  | 1050 | 800 | 1500 | 1100
| * | Vented-fan cooled. ( |  |  | SCFM) | 0 |  | 787SS / 797SS | NEMA 4X | 850 | 700 | 1120 | 900 | 1700 | 1300
|  | Vented-no fan. | [5 empty] | 7735 | NEMA 4X |  |  | 1600 | 1250 | 2500 | 1600
[8 empty] | 787SS-35H / 797SS-35H | NEMA 4X | 1200 | 900 | 1600 | 1250 | 2500 | 1600
[8 empty] | 7875SS / 7975SS / 7770 | NEMA 4X | 2400 | 1800 | 3200 | 2500 | 5000 | 3200
Note: If the compressed air supply is not dried to a -40 degree F pressure dew point, devalue
|  | *Temperature of air entering enclosure (F). | [5 empty] | capacities by 15%. Compressed air temperatures must not exceed 110 degrees F.
| If fan cooled: | [6 empty] | If compressed air temperatures exceed 110 degrees F, call the factory.
*Temperature of air exiting enclosure (F).
Note: "BTUH" capacity when compressed air temperature does not exceed 70 degrees F.
">70 degrees F" capacity when compressed air temperature exceeds 70 degrees F.
Note: The models listed above which have a 770 prefix and the Vortex A/C models (listed in blue) all feature a
highly reliable, mechanical thermostat to maintain cabinet temperatures within a range of 80 to 90 degrees F.
** A minimum of 80 psi is required for proper operation of this thermostat.
Note on C3: Enter the Height of the cabinet in inches.
Note on C4: Enter the width of the cabinet in inches.
Note on H4: This is the square footage of your enclosure based on the H, W & D that you enter.
Note on C5: Enter the depth of the cabinet in inches.
Note on C7: Enter the internal temperature of the cabinet. If unknown, go to the "Dissipated Heat in Watts" box.
Note on E7: Enter the temperature of the surrounding air. If unknown, go to the "Dissipated Heat in Watts" box.
Note on C9: Enter the temperature that you would like to maintain inside of the cabinet.
Note on E9: Enter the highest surrounding temperature that the cabinet will be exposed to.
Note on C11: If you don't know the internal temp and ambient temp, you need to obtain the dissipated watts rating for each component inside of the cabinet. This can usually be obtained from the manufacturer of the components. Keep in mind, this is not the total energy consumption of the components, but the amount of energy that is lost in the form of heat.
Note on H15: If the cabinet is exposed to direct sunlight, enter the number that corresponds to the color that matches the cabinet. If not exposed to direct sunlight, leave this box blank.
Note on H17: This is the total BTUH of cooling that you need to provide in order to maintain the desired temperature that you specified.
Note on E27: If your cabinet is fan cooled, enter the total SCFM rating(s) of fan(s) that are used to pull air through the cabinet. If not fan cooled, leave this box blank.
Note on G27: This is the total BTUH of cooling provided by the fans in your cabinet. This is included in the "Total BTUH" box. It is figured by multiplying the SCFM of the fan(s), by the temp difference of the air exiting and the air entering, by 1.08.
Note on G33: If your cabinet is fan cooled, enter the temperature of the air entering the enclosure. If not fan cooled, leave this box blank.
Note on G35: If your cabinet is fan cooled, enter the temperature of the air exiting the enclosure. If not fan cooled, leave this box blank